CIRCUIT CONFIGURATIONS

---
CIRCUIT CONFIGURATIONS
Learning Outcomes
At the end of this session you should be able to:
Draw
a one way and a two way controlled lighting circuit
a radial socket circuit
a dedicated radial circuit
a socket outlet ring main circuit
State a use for each type of circuit.

---
One Way & Two Way controlled lighting circuit
One way lighting circuit
The type of lighting point termination for the wiring system used in our maintenance tasks is a batten lampholder to BS EN 60598.
Lighting circuits can be wired with either 1mm2 or 1.5mm2 cable

---
One Way & Two Way controlled lighting circuit - continued
Two Way Lighting Circuit

---
Radial Final Circuit
A radial final circuit starts at the distribution board, where it is connected to an overcurrent protective device, then it is wired to the equipment; looping in and then looping out.
(BS 7671 Appendix 15 Fig 15B)
This circuit is known as an A3 radial because:
Overcurrent protective device is only 20A
Wired in 2.5mm2
Serving a floor area not exceeding 50m2
Using BS 1363 socket-outlets

---
Radial Final Circuit – continued
Another radial circuit known as an A2 has the following characteristics:
Overcurrent protective device is either 30A or 32A
Wired in 4.0mm2
Serving a floor area not exceeding 75m2
Using BS 1363 socket-outlets
The A3 and A2 circuits only comply to socket-outlets and fused connection units (FCU)
Other radial circuits like,
Lighting
Power circuits
Have other factors to take into consideration like current-carrying capacites, voltage drop and reference methods (Appendix F on-site-guide BS7671).

---
Dedicated Radial Final Circuit – continued
These circuits are encountered where a security of supply makes it prudent to separate from other circuits that may become faulty, such a circuit is a fire alarm circuit.
Alternatively they may be used where larger loads are encountered such as cookers, immersion heaters or comprehensive space heating appliances.
Beyond the circuit fuse there is usually no further protective devices.

---
Ring Final Circuit
‘A final circuit arranged in the form of a ring and connected to a single point of supply’
Taken from BS 7671:2008 Amendment 3:2015 Part 2 Definitions
A ring final circuit starts and finishes at the distribution board, where it is connected to a 30 A or 32 A overcurrent protective device.
Total floor area being served is 100 m2.
Equipment that is designed to stay on for long periods, cookers, ovens and hobs that exceed 2KW should be put on their own dedicated radial circuit.

---
Ring Final Circuit – continued
A1 Ring
(Table H2.1 BS 7671 on-site-guide)
Minimum Copper Conductor CSA:
Thermoplastic or Thermosetting insulated cables CSA 2.5mm2
Mineral Insulated Cables CSA 1.5mm2
30 or 32 amp overcurrent Protective device
Maximum area to be served = 100 M2
BS 1363 socket-outlets.
Appendix 15 BS 7671:2008 Amendment 3:2015

---
Ring Final Circuit – continued
Unfused Spurs (spurs directly connected to the ring)
The size of the cable used for spurs are usually the same as that of the ring circuit, in order that the cable is not overloaded the regulations permit only one single, one twin socket outlet or one item of stationary equipment on each spur.
The number of spurred circuits should not exceed the number of sockets on the ring.

---
Fused Spurs
In the case of fused spurs the fuse ensures that the cable will not carry a current in excess of its maximum rating hence there is no limit on the number of sockets that may be connected.
Care must be taken however that the fuse size is not exceeded.